## bus
| name | vn_kv | type | zone | in_service | geo
0 | BQPS_COMMON | 220 | b |  | TRUE | null
1 | KCR | 220 | b |  | TRUE | null
2 | LALAZAR | 220 | b |  | TRUE | null
3 | BALDIA | 220 | b |  | TRUE | null
4 | NKI / NK1 | 220 | b |  | TRUE | null
5 | KDA | 220 | b |  | TRUE | null
6 | PIPRI WEST | 220 | b |  | TRUE | null
7 | MAURIPUR | 220 | b |  | TRUE | null
8 | ICI | 220 | b |  | TRUE | null
9 | JAMSHORO-1 | 220 | b |  | TRUE | null
10 | JAMSHORO-2 | 220 | b |  | TRUE | null
11 | HUBCO | 220 | b |  | TRUE | null
12 | UTHAL | 66 | b |  | TRUE | null
13 | BELA | 66 | b |  | TRUE | null
14 | VINDER | 132 | b |  | TRUE | null
15 | HUB CHOWKI | 132 | b |  | TRUE | null
16 | BALDIA | 132 | b |  | TRUE | null
17 | ATTOCK CEMENT | 132 | b |  | TRUE | null
18 | TAPAL | 132 | b |  | TRUE | null
19 | KANUPP | 132 | b |  | TRUE | null
20 | SGT / SGTPS | 132 | b |  | TRUE | null
21 | SITE | 132 | b |  | TRUE | null
22 | HAROONABAD | 132 | b |  | TRUE | null
23 | LYARI | 132 | b |  | TRUE | null
24 | WEST WHARF | 132 | b |  | TRUE | null
25 | ORANGI TOWN | 132 | b |  | TRUE | null
26 | VALIKA | 132 | b |  | TRUE | null
27 | NORTH KARACHI | 132 | b |  | TRUE | null
28 | LIAQUATABAD | 132 | b |  | TRUE | null
29 | NORTH NAZIMABAD | 132 | b |  | TRUE | null
30 | OLD TOWN | 132 | b |  | TRUE | null
31 | CREEK CITY | 132 | b |  | TRUE | null
32 | DHA-1 | 132 | b |  | TRUE | null
33 | DEFENCE | 132 | b |  | TRUE | null
34 | QUEENS ROAD | 132 | b |  | TRUE | null
35 | CLIFTON | 132 | b |  | TRUE | null
36 | GIZRI | 132 | b |  | TRUE | null
37 | GARDEN EAST | 132 | b |  | TRUE | null
38 | ELENDER ROAD | 132 | b |  | TRUE | null
39 | JACOBLINE | 132 | b |  | TRUE | null
40 | QAYYUMABAD | 132 | b |  | TRUE | null
41 | KORANGI EAST | 132 | b |  | TRUE | null
42 | KORANGI WEST | 132 | b |  | TRUE | null
43 | KORANGI SOUTH | 132 | b |  | TRUE | null
44 | AIRPORT-2 | 132 | b |  | TRUE | null
45 | CIVIC CENTER | 132 | b |  | TRUE | null
46 | AZIZABAD | 132 | b |  | TRUE | null
47 | JAIL ROAD | 132 | b |  | TRUE | null
48 | GULSHAN | 132 | b |  | TRUE | null
49 | KESC HOSPITAL | 132 | b |  | TRUE | null
50 | GULISTAN E JOHAR | 132 | b |  | TRUE | null
51 | SURJANI TOWN | 132 | b |  | TRUE | null
52 | GULSHAN-E-MAYMAR | 132 | b |  | TRUE | null
53 | FEDERAL A | 132 | b |  | TRUE | null
54 | FEDERAL B | 132 | b |  | TRUE | null
55 | KDA SCHEME 33 / KDA | 132 | b |  | TRUE | null
56 | MEMON GOTH | 132 | b |  | TRUE | null
57 | MALIR | 132 | b |  | TRUE | null
58 | CAA | 132 | b |  | TRUE | null
59 | GHARO | 132 | b |  | TRUE | null
60 | DHABEJI | 132 | b |  | TRUE | null
61 | BOC | 132 | b |  | TRUE | null
62 | RECP | 132 | b |  | TRUE | null
63 | PIPRI WEST | 132 | b |  | TRUE | null
64 | LANDHI | 132 | b |  | TRUE | null
65 | PORT QASIM | 132 | b |  | TRUE | null
66 | KEPZ | 132 | b |  | TRUE | null
67 | PIPRI EAST / F.EAST | 132 | b |  | TRUE | null
68 | STEEL-1 | 132 | b |  | TRUE | null
69 | STEEL-2 | 132 | b |  | TRUE | null
70 | PRL | 132 | b |  | TRUE | null
71 | KORANGI TOWN | 132 | b |  | TRUE | null
72 | BALOCH COLONY | 132 | b |  | TRUE | null
73 | JSKY_MAURIPUR_132 | 132 | b |  | TRUE | null
74 | SP_STEEL_TAP | 132 | b |  | TRUE | null
75 | J_CEMENT_TAP | 132 | b |  | TRUE | null
76 | BQPS_I_220 | 220 | b |  | TRUE | null
77 | BQPS_II_220 | 220 | b |  | TRUE | null
78 | KTPS_CCP_220 | 220 | b |  | TRUE | null
79 | KARKEY_220 | 220 | b |  | TRUE | null
80 | CCP_220 | 220 | b |  | TRUE | null
81 | GADAP_60 | 60 | b |  | TRUE | null
82 | GADAP_132 | 132 | b |  | FALSE | null
83 | PAPCO_TAP | 132 | b |  | TRUE | null
84 | DCL_132 | 132 | b |  | TRUE | null
85 | GUL_AHMED_132 | 132 | b |  | TRUE | null
86 | KTPS_132 | 132 | b |  | TRUE | null
87 | AIRPORT | 132 | b |  | TRUE | null
88 | KORANGI | 132 | b |  | TRUE | null
89 | P_MAN | 132 | b |  | FALSE | null
90 | AASML_11 | 11 | b |  | TRUE | null
91 | EPCL_11 | 11 | b |  | TRUE | null
92 | IIL1_11 | 11 | b |  | TRUE | null
93 | IIL2_11 | 11 | b |  | TRUE | null
94 | PASMIC_11 | 11 | b |  | TRUE | null
95 | KGT_SEC1_11 | 11 | b |  | TRUE | null
96 | KGT_SEC2_11 | 11 | b |  | TRUE | null
97 | KGT_SEC3_11 | 11 | b |  | TRUE | null
98 | KGT_SEC4_11 | 11 | b |  | TRUE | null
99 | KGT_OLD_11 | 11 | b |  | TRUE | null
100 | APGL_11 | 11 | b |  | TRUE | null

## load
| name | bus | p_mw | q_mvar | const_z_p_percent | const_i_p_percent | const_z_q_percent | const_i_q_percent | sn_mva | scaling | in_service | type
0 | LOAD_UTHAL | 12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
1 | LOAD_BELA | 13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
2 | LOAD_VINDER | 14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
3 | LOAD_HUB CHOWKI | 15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
4 | LOAD_BALDIA | 16 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
5 | LOAD_ATTOCK CEMENT | 17 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
6 | LOAD_TAPAL | 18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
7 | LOAD_KANUPP | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
8 | LOAD_SGT / SGTPS | 20 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
9 | LOAD_SITE | 21 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
10 | LOAD_HAROONABAD | 22 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
11 | LOAD_LYARI | 23 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
12 | LOAD_WEST WHARF | 24 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
13 | LOAD_ORANGI TOWN | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
14 | LOAD_VALIKA | 26 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
15 | LOAD_NORTH KARACHI | 27 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
16 | LOAD_LIAQUATABAD | 28 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
17 | LOAD_NORTH NAZIMABAD | 29 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
18 | LOAD_OLD TOWN | 30 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
19 | LOAD_CREEK CITY | 31 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
20 | LOAD_DHA-1 | 32 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
21 | LOAD_DEFENCE | 33 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
22 | LOAD_QUEENS ROAD | 34 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
23 | LOAD_CLIFTON | 35 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
24 | LOAD_GIZRI | 36 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
25 | LOAD_GARDEN EAST | 37 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
26 | LOAD_ELENDER ROAD | 38 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
27 | LOAD_JACOBLINE | 39 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
28 | LOAD_QAYYUMABAD | 40 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
29 | LOAD_KORANGI EAST | 41 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
30 | LOAD_KORANGI WEST | 42 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
31 | LOAD_KORANGI SOUTH | 43 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
32 | LOAD_AIRPORT-2 | 44 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
33 | LOAD_CIVIC CENTER | 45 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
34 | LOAD_AZIZABAD | 46 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
35 | LOAD_JAIL ROAD | 47 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
36 | LOAD_GULSHAN | 48 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
37 | LOAD_KESC HOSPITAL | 49 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
38 | LOAD_GULISTAN E JOHAR | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
39 | LOAD_SURJANI TOWN | 51 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
40 | LOAD_GULSHAN-E-MAYMAR | 52 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
41 | LOAD_FEDERAL A | 53 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
42 | LOAD_FEDERAL B | 54 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
43 | LOAD_KDA SCHEME 33 / KDA | 55 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
44 | LOAD_MEMON GOTH | 56 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
45 | LOAD_MALIR | 57 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
46 | LOAD_CAA | 58 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
47 | LOAD_GHARO | 59 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
48 | LOAD_DHABEJI | 60 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
49 | LOAD_BOC | 61 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
50 | LOAD_RECP | 62 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
51 | LOAD_PIPRI WEST | 63 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
52 | LOAD_LANDHI | 64 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
53 | LOAD_PORT QASIM | 65 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
54 | LOAD_KEPZ | 66 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
55 | LOAD_PIPRI EAST / F.EAST | 67 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
56 | LOAD_STEEL-1 | 68 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
57 | LOAD_STEEL-2 | 69 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
58 | LOAD_PRL | 70 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
59 | LOAD_KORANGI TOWN | 71 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
60 | LOAD_BALOCH COLONY | 72 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
61 | LOAD_JSKY_MAURIPUR_132 | 73 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
62 | LOAD_SP_STEEL_TAP | 74 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
63 | LOAD_J_CEMENT_TAP | 75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
64 | LOAD_GADAP_132 | 82 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
65 | LOAD_PAPCO_TAP | 83 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
66 | LOAD_DCL_132 | 84 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
67 | LOAD_GUL_AHMED_132 | 85 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
68 | LOAD_KTPS_132 | 86 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
69 | LOAD_AIRPORT | 87 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
70 | LOAD_KORANGI | 88 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
71 | LOAD_P_MAN | 89 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
72 | LOAD_AASML_11 | 90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
73 | LOAD_EPCL_11 | 91 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
74 | LOAD_IIL1_11 | 92 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
75 | LOAD_IIL2_11 | 93 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
76 | LOAD_PASMIC_11 | 94 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
77 | LOAD_KGT_SEC1_11 | 95 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
78 | LOAD_KGT_SEC2_11 | 96 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
79 | LOAD_KGT_SEC3_11 | 97 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
80 | LOAD_KGT_SEC4_11 | 98 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
81 | LOAD_KGT_OLD_11 | 99 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye
82 | LOAD_APGL_11 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | TRUE | wye

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | controllable | id_q_capability_characteristic | reactive_capability_curve | curve_style | in_service | slack_weight | type | min_p_mw | max_p_mw | source_type
0 | B_EXT_JAMSHORO2 | 10 | 500 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 2050 | external_import
1 | B_EXT_HUBCO | 11 | 325 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 650 | external_import
2 | G_BQPS_I | 76 | 1260 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 1260
3 | G_BQPS_II | 77 | 560 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 560
4 | G_KTPS_132 | 86 | 125 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 125
5 | G_KTPS_CCP | 78 | 220 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 220
6 | G_KGT_SEC1_11 | 95 | 21.92 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 21.92
7 | G_SGTPS | 20 | 88 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 88
8 | G_KGT_OLD | 99 | 20 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 20
9 | G_APGL | 100 | 7.92 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 7.92
10 | G_GUL_AHMED | 85 | 136.17 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 136.17
11 | G_TAPAL | 18 | 126 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 126
12 | G_KANUPP | 19 | 125 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 125
13 | G_AASML | 90 | 13 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 13
14 | G_EPCL | 91 | 18 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 18
15 | G_IIL1 | 92 | 4 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 4
16 | G_IIL2 | 93 | 18 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 18
17 | G_PASMIC | 94 | 165 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 165
18 | G_KARKEY | 79 | 231.8 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 231.8
19 | G_DCL | 84 | 80.3 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 80.3
20 | G_KGT_SEC2_11 | 96 | 21.92 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 21.92
21 | G_KGT_SEC3_11 | 97 | 21.92 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 21.92
22 | G_KGT_SEC4_11 | 98 | 21.92 | 1 |  |  |  | 1 | FALSE | TRUE |  | FALSE |  | TRUE | 0 |  | 0 | 21.92

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | controllable
0 | B_EXT_JAMSHORO1 | 9 | 1 | 0 | 1 | TRUE | FALSE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | geo | thermal_role
0 | L220_JICA_01 | 490-AL1/64-ST1A 220.0 | 0 | 1 | 35.5 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
1 | L220_JICA_02 | 490-AL1/64-ST1A 220.0 | 0 | 1 | 35.5 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
2 | L220_JICA_03 | 490-AL1/64-ST1A 220.0 | 0 | 6 | 8.693 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
3 | L220_JICA_04 | 490-AL1/64-ST1A 220.0 | 0 | 6 | 8.693 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
4 | L220_JICA_05 | 490-AL1/64-ST1A 220.0 | 0 | 6 | 8.57 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
5 | L220_JICA_06 | 490-AL1/64-ST1A 220.0 | 0 | 8 | 0.36 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
6 | L220_JICA_07 | 490-AL1/64-ST1A 220.0 | 8 | 6 | 8.502 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
7 | L220_JICA_08 | 490-AL1/64-ST1A 220.0 | 6 | 5 | 30.708 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
8 | L220_JICA_09 | 490-AL1/64-ST1A 220.0 | 6 | 5 | 30.708 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
9 | L220_JICA_10 | 490-AL1/64-ST1A 220.0 | 5 | 3 | 30.939 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
10 | L220_JICA_11 | 490-AL1/64-ST1A 220.0 | 5 | 4 | 30.75 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
11 | L220_JICA_12 | 490-AL1/64-ST1A 220.0 | 3 | 4 | 14.41 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
12 | L220_JICA_13 | 490-AL1/64-ST1A 220.0 | 1 | 2 | 9.47 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
13 | L220_JICA_14 | 490-AL1/64-ST1A 220.0 | 1 | 2 | 9.47 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
14 | L220_JICA_15 | 490-AL1/64-ST1A 220.0 | 2 | 7 | 6.987 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
15 | L220_JICA_16 | 490-AL1/64-ST1A 220.0 | 2 | 7 | 6.987 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
16 | L220_JICA_17 | 490-AL1/64-ST1A 220.0 | 3 | 7 | 21.815 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
17 | L220_JICA_18 | 490-AL1/64-ST1A 220.0 | 3 | 7 | 21.815 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
18 | L220_JICA_19 | 490-AL1/64-ST1A 220.0 | 1 | 80 | 9.069 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
19 | L220_SLD_KCR_CCP_II | 490-AL1/64-ST1A 220.0 | 1 | 80 | 9.069 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
20 | L220_EXT_KDA_JAMSHORO_1 | 490-AL1/64-ST1A 220.0 | 9 | 5 | 130 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
21 | L220_EXT_KDA_JAMSHORO_2 | 490-AL1/64-ST1A 220.0 | 10 | 5 | 130 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
22 | L220_EXT_HUBCO_NKI_1 | 490-AL1/64-ST1A 220.0 | 11 | 4 | 27 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
23 | L220_EXT_HUBCO_NKI_2 | 490-AL1/64-ST1A 220.0 | 11 | 4 | 27 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
24 | L220_GEN_BQPS_I_TIE | 490-AL1/64-ST1A 220.0 | 76 | 0 | 0.001 | 0.059 | 0.285 | 10 | 0 | 9999 | 1 | 1 | ol | TRUE | null | busbar_tie_excluded
25 | L220_GEN_BQPS_II_TIE | 490-AL1/64-ST1A 220.0 | 77 | 0 | 0.001 | 0.059 | 0.285 | 10 | 0 | 9999 | 1 | 1 | ol | TRUE | null | busbar_tie_excluded
26 | L220_GEN_KTPS_CCP_TIE | 490-AL1/64-ST1A 220.0 | 78 | 80 | 0.001 | 0.059 | 0.285 | 10 | 0 | 9999 | 1 | 1 | ol | TRUE | null | busbar_tie_excluded
27 | L220_GEN_KARKEY_TIE | 490-AL1/64-ST1A 220.0 | 79 | 78 | 1 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
28 | L132_JICA_01 | 490-AL1/64-ST1A 110.0 | 86 | 64 | 13.3 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
29 | L132_JICA_02 | 490-AL1/64-ST1A 110.0 | 86 | 64 | 12.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
30 | L132_JICA_03 | 490-AL1/64-ST1A 110.0 | 40 | 41 | 10.875 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
31 | L132_JICA_04 | 490-AL1/64-ST1A 110.0 | 40 | 41 | 10.8 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
32 | L132_JICA_05 | 490-AL1/64-ST1A 110.0 | 86 | 70 | 2.476 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
33 | L132_JICA_06 | 490-AL1/64-ST1A 110.0 | 70 | 42 | 6.011 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
34 | L132_JICA_07 | 490-AL1/64-ST1A 110.0 | 71 | 42 | 7.281 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
35 | L132_JICA_08 | 490-AL1/64-ST1A 110.0 | 71 | 72 | 8.655 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
36 | L132_JICA_09 | 490-AL1/64-ST1A 110.0 | 42 | 33 | 5.988 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
37 | L132_JICA_10 | 490-AL1/64-ST1A 110.0 | 33 | 36 | 6.956 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
38 | L132_JICA_11_A | 490-AL1/64-ST1A 110.0 | 36 | 72 | 4.2045 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
39 | L132_JICA_11_B | 490-AL1/64-ST1A 110.0 | 36 | 42 | 4.2045 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
40 | L132_JICA_12 | 490-AL1/64-ST1A 110.0 | 36 | 35 | 3.413 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
41 | L132_JICA_13 | 490-AL1/64-ST1A 110.0 | 35 | 34 | 5.723 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
42 | L132_JICA_14 | 490-AL1/64-ST1A 110.0 | 36 | 34 | 4.856 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
43 | L132_JICA_15 | 490-AL1/64-ST1A 110.0 | 63 | 61 | 16.258 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
44 | L132_JICA_16 | 490-AL1/64-ST1A 110.0 | 61 | 60 | 18.586 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
45 | L132_JICA_17 | 490-AL1/64-ST1A 110.0 | 60 | 59 | 12.502 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
46 | L132_JICA_18 | 490-AL1/64-ST1A 110.0 | 63 | 62 | 7.858 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
47 | L132_JICA_19 | 490-AL1/64-ST1A 110.0 | 62 | 59 | 33.344 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
48 | L132_JICA_20 | 490-AL1/64-ST1A 110.0 | 63 | 64 | 14.13 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
49 | L132_JICA_21 | 490-AL1/64-ST1A 110.0 | 63 | 65 | 4.19 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
50 | L132_JICA_22 | 490-AL1/64-ST1A 110.0 | 65 | 64 | 9.95 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
51 | L132_JICA_23 | 490-AL1/64-ST1A 110.0 | 63 | 71 | 21.989 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
52 | L132_JICA_24 | 490-AL1/64-ST1A 110.0 | 63 | 66 | 12.104 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
53 | L132_JICA_25 | 490-AL1/64-ST1A 110.0 | 66 | 64 | 7.385 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
54 | L132_JICA_26 | 490-AL1/64-ST1A 110.0 | 64 | 85 | 7.46 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
55 | L132_JICA_27 | 490-AL1/64-ST1A 110.0 | 71 | 85 | 0.35 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
56 | L132_JICA_28 | 490-AL1/64-ST1A 110.0 | 85 | 87 | 2.27 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
57 | L132_JICA_29 | 490-AL1/64-ST1A 110.0 | 85 | 87 | 2.27 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
58 | L132_JICA_30 | 490-AL1/64-ST1A 110.0 | 64 | 58 | 15.1 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
59 | L132_JICA_31 | 490-AL1/64-ST1A 110.0 | 58 | 57 | 5.857 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
60 | L132_JICA_32 | 490-AL1/64-ST1A 110.0 | 55 | 56 | 14.2 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
61 | L132_JICA_33 | 490-AL1/64-ST1A 110.0 | 56 | 57 | 6.675 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
62 | L132_JICA_34 | 490-AL1/64-ST1A 110.0 | 57 | 50 | 7.56 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
63 | L132_JICA_35_A | 490-AL1/64-ST1A 110.0 | 64 | 50 | 13.396 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
64 | L132_JICA_35_B | 490-AL1/64-ST1A 110.0 | 64 | 48 | 13.396 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
65 | L132_JICA_36 | 490-AL1/64-ST1A 110.0 | 55 | 50 | 6.72 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
66 | L132_JICA_37 | 490-AL1/64-ST1A 110.0 | 55 | 48 | 11.36 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
67 | L132_JICA_38 | 490-AL1/64-ST1A 110.0 | 55 | 52 | 5.8 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
68 | L132_JICA_39 | 490-AL1/64-ST1A 110.0 | 52 | 51 | 5.471 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
69 | L132_JICA_40 | 490-AL1/64-ST1A 110.0 | 26 | 51 | 7.171 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
70 | L132_JICA_41 | 490-AL1/64-ST1A 110.0 | 55 | 54 | 14.7 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
71 | L132_JICA_42_A | 490-AL1/64-ST1A 110.0 | 54 | 26 | 5.35 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
72 | L132_JICA_42_B | 490-AL1/64-ST1A 110.0 | 54 | 53 | 5.35 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
73 | L132_JICA_43 | 490-AL1/64-ST1A 110.0 | 27 | 26 | 3.15 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
74 | L132_JICA_44 | 490-AL1/64-ST1A 110.0 | 27 | 26 | 3.15 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
75 | L132_JICA_45 | 490-AL1/64-ST1A 110.0 | 16 | 26 | 11.8 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
76 | L132_JICA_46 | 490-AL1/64-ST1A 110.0 | 16 | 25 | 6.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
77 | L132_TAP_ORANGI_SPSTEEL | 490-AL1/64-ST1A 110.0 | 25 | 74 | 3.2 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
78 | L132_TAP_SPSTEEL_JCEMENT | 490-AL1/64-ST1A 110.0 | 74 | 75 | 2.8 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
79 | L132_TAP_JCEMENT_VALIKA | 490-AL1/64-ST1A 110.0 | 75 | 26 | 3.69 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
80 | L132_JICA_48 | 490-AL1/64-ST1A 110.0 | 26 | 29 | 6.43 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
81 | L132_JICA_49 | 490-AL1/64-ST1A 110.0 | 29 | 22 | 5.88 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
82 | L132_JICA_50 | 490-AL1/64-ST1A 110.0 | 26 | 28 | 11.25 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
83 | L132_JICA_51 | 490-AL1/64-ST1A 110.0 | 28 | 22 | 10.28 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
84 | L132_JICA_52 | 490-AL1/64-ST1A 110.0 | 73 | 22 | 6.158 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
85 | L132_JICA_53 | 490-AL1/64-ST1A 110.0 | 73 | 22 | 6.158 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
86 | L132_JICA_54 | 490-AL1/64-ST1A 110.0 | 16 | 20 | 4.3 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
87 | L132_JICA_55_A | 490-AL1/64-ST1A 110.0 | 16 | 20 | 2.485 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
88 | L132_JICA_55_B | 490-AL1/64-ST1A 110.0 | 16 | 21 | 2.485 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
89 | L132_JICA_56 | 490-AL1/64-ST1A 110.0 | 20 | 21 | 0.67 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
90 | L132_JICA_57 | 490-AL1/64-ST1A 110.0 | 16 | 19 | 21.078 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
91 | L132_JICA_58 | 490-AL1/64-ST1A 110.0 | 16 | 19 | 21.078 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
92 | L132_JICA_59 | 490-AL1/64-ST1A 110.0 | 16 | 15 | 16 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
93 | L132_JICA_60 | 490-AL1/64-ST1A 110.0 | 16 | 18 | 8.48 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
94 | L132_JICA_61 | 490-AL1/64-ST1A 110.0 | 18 | 15 | 8.48 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
95 | L132_JICA_62 | 490-AL1/64-ST1A 110.0 | 15 | 14 | 42.9 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
96 | L132_JICA_63 | 490-AL1/64-ST1A 110.0 | 41 | 44 | 2.312 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
97 | L132_JICA_64 | 490-AL1/64-ST1A 110.0 | 41 | 44 | 2.312 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
98 | L132_JICA_65 | 490-AL1/64-ST1A 110.0 | 43 | 88 | 4.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
99 | L132_SLD_HUBCHOWKI_ATTOCK | 490-AL1/64-ST1A 110.0 | 15 | 17 | 9 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
100 | L132_SLD_SGT_SITE_I | 490-AL1/64-ST1A 110.0 | 20 | 21 | 1 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
101 | L132_SLD_SGT_HAROON_I_UG | 490-AL1/64-ST1A 110.0 | 20 | 22 | 4 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
102 | L132_SLD_SGT_HAROON_II_UG | 490-AL1/64-ST1A 110.0 | 20 | 22 | 4 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
103 | L132_SLD_SGT_LYARI_UG | 490-AL1/64-ST1A 110.0 | 20 | 23 | 7 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
104 | L132_SLD_LYARI_WWHARF_UG | 490-AL1/64-ST1A 110.0 | 23 | 24 | 2.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
105 | L132_SLD_SITE_HAROON_UG | 490-AL1/64-ST1A 110.0 | 21 | 22 | 3 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
106 | L132_SLD_WWHARF_OLDTOWN_UG | 490-AL1/64-ST1A 110.0 | 24 | 30 | 4 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
107 | L132_SLD_OLDTOWN_QROAD_UG | 490-AL1/64-ST1A 110.0 | 30 | 34 | 2 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
108 | L132_SLD_QAY_KTPS | 490-AL1/64-ST1A 110.0 | 40 | 86 | 4.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
109 | L132_SLD_QAY_KWEST_U1_UG | 490-AL1/64-ST1A 110.0 | 40 | 42 | 5.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
110 | L132_SLD_QAY_KWEST_U2_UG | 490-AL1/64-ST1A 110.0 | 40 | 42 | 5.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
111 | L132_SLD_QAY_DHA_UG | 490-AL1/64-ST1A 110.0 | 40 | 32 | 4.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
112 | L132_SLD_DHA_CREEK_UG | 490-AL1/64-ST1A 110.0 | 32 | 31 | 6 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
113 | L132_SLD_CREEK_DCL_UG | 490-AL1/64-ST1A 110.0 | 31 | 84 | 5.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
114 | L132_SLD_DCL_DEFENCE_UG | 490-AL1/64-ST1A 110.0 | 84 | 33 | 7 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
115 | L132_SLD_GIZRI_JACOB_UG | 490-AL1/64-ST1A 110.0 | 36 | 39 | 7 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
116 | L132_SLD_JACOB_BALOCH_UG | 490-AL1/64-ST1A 110.0 | 39 | 72 | 4.8 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
117 | L132_SLD_JACOB_GARDEN_UG | 490-AL1/64-ST1A 110.0 | 39 | 37 | 2 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
118 | L132_SLD_QROAD_ELENDER_I_UG | 490-AL1/64-ST1A 110.0 | 34 | 38 | 1.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
119 | L132_SLD_QROAD_ELENDER_II_UG | 490-AL1/64-ST1A 110.0 | 34 | 38 | 1.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
120 | L132_SLD_LABAD_CCENTRE | 490-AL1/64-ST1A 110.0 | 28 | 45 | 3 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
121 | L132_SLD_LABAD_AZIZ | 490-AL1/64-ST1A 110.0 | 28 | 46 | 2.24 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
122 | L132_SLD_CCENTRE_GULSHAN_I | 490-AL1/64-ST1A 110.0 | 45 | 48 | 2.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
123 | L132_SLD_CCENTRE_GULSHAN_II | 490-AL1/64-ST1A 110.0 | 45 | 48 | 2.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
124 | L132_SLD_AZIZ_GULSHAN | 490-AL1/64-ST1A 110.0 | 46 | 48 | 5.15 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
125 | L132_SLD_GULSHAN_JAIL_I | 490-AL1/64-ST1A 110.0 | 48 | 47 | 7.4 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
126 | L132_SLD_GULSHAN_JAIL_II | 490-AL1/64-ST1A 110.0 | 48 | 47 | 7.4 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
127 | L132_SLD_GULSHAN_HOSPITAL | 490-AL1/64-ST1A 110.0 | 48 | 49 | 4 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
128 | L132_SLD_HOSPITAL_JOHAR | 490-AL1/64-ST1A 110.0 | 49 | 50 | 4 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
129 | L132_SLD_KEAST_KSOUTH | 490-AL1/64-ST1A 110.0 | 41 | 43 | 3.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
130 | L132_SLD_KSOUTH_KTPS | 490-AL1/64-ST1A 110.0 | 43 | 86 | 5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
131 | L132_SLD_PAPCO_PQASIM | 490-AL1/64-ST1A 110.0 | 83 | 65 | 3 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
132 | L132_SLD_PIPRIWEST_FEAST | 490-AL1/64-ST1A 110.0 | 63 | 67 | 3.5 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
133 | L132_SLD_PIPRIWEST_STEEL1 | 490-AL1/64-ST1A 110.0 | 63 | 68 | 6 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
134 | L132_SLD_PIPRIWEST_STEEL2 | 490-AL1/64-ST1A 110.0 | 63 | 69 | 6 | 0.059 | 0.37 | 9.75 | 0 | 0.96 | 1 | 1 | ol | TRUE | null
135 | L66_SLD_BELA_UTHAL | 243-AL1/39-ST1A 110.0 | 13 | 12 | 60 | 0.1188 | 0.39 | 9 | 0 | 0.645 | 1 | 1 | ol | TRUE | null

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_changer_type | id_characteristic_table | tap_dependency_table | parallel | df | in_service | oltc
0 | T_BALDIA_1 |  | 3 | 16 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
1 | T_BALDIA_2 |  | 3 | 16 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
2 | T_NKI_1 |  | 4 | 27 | 800 | 220 | 132 | 14 | 0.25 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
3 | T_NKI_2 |  | 4 | 27 | 800 | 220 | 132 | 14 | 0.25 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
4 | T_KDA_1 |  | 5 | 55 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
5 | T_KDA_2 |  | 5 | 55 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
6 | T_KDA_3 |  | 5 | 55 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
7 | T_MAURIPUR_JSKY |  | 7 | 73 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
8 | T_LALAZAR_1 |  | 2 | 34 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
9 | T_LALAZAR_2 |  | 2 | 34 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
10 | T_PIPRIWEST_1 |  | 6 | 63 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
11 | T_PIPRIWEST_2 |  | 6 | 63 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
12 | T_PIPRIWEST_3 |  | 6 | 63 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
13 | T_KCR_KWEST |  | 1 | 42 | 250 | 220 | 132 | 12 | 0.3 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
14 | T_VINDER_UTHAL |  | 14 | 12 | 60 | 132 | 60 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
15 | T_MALIR_GADAP |  | 57 | 81 | 40 | 132 | 60 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
16 | T_DHABEJI_AASML |  | 60 | 90 | 20 | 132 | 11 | 8 | 0.5 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
17 | T_BOC_EPCL |  | 61 | 91 | 20 | 132 | 11 | 8 | 0.5 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
18 | T_KEPZ_IIL1_RATING_UNKNOWN |  | 66 | 92 | 100 | 132 | 11 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
19 | T_LANDHI_IIL2_RATING_UNKNOWN |  | 64 | 93 | 100 | 132 | 11 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
20 | T_FEAST_PASMIC_1_RATING_UNKNOWN |  | 67 | 94 | 100 | 132 | 11 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
21 | T_FEAST_PASMIC_2_RATING_UNKNOWN |  | 67 | 94 | 100 | 132 | 11 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
22 | T_KTOWN_KGT_SEC1_RATING_UNKNOWN |  | 71 | 95 | 100 | 132 | 11 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
23 | T_KTOWN_KGT_SEC2_RATING_UNKNOWN |  | 71 | 96 | 100 | 132 | 11 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
24 | T_KTOWN_KGT_SEC3_RATING_UNKNOWN |  | 71 | 97 | 100 | 132 | 11 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
25 | T_KTOWN_KGT_SEC4_RATING_UNKNOWN |  | 71 | 98 | 100 | 132 | 11 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
26 | T_KTOWN_KGT_OLD_RATING_UNKNOWN |  | 71 | 99 | 100 | 132 | 11 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE
27 | T_KTOWN_APGL_RATING_UNKNOWN |  | 71 | 100 | 100 | 132 | 11 | 10 | 0.4 | 0 | 0 | 0 | [9 empty] | FALSE | 1 | 1 | TRUE | FALSE

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## line_dc_std_types
| r_ohm_per_km | max_i_ka | type | q_mm2 | alpha
95-CU | 0.193 | 0.404 | cs | 95 | 0.00393
400-CU | 0.047 | 0.922 | cs | 400 | 0.00393
1200-CU | 0.0151 | 1.791 | cs | 1200 | 0.00393
2400-CU | 0.0073 | 2.678 | cs | 2400 | 0.00393
95-AL | 0.32 | 0.31 | cs | 95 | 0.00403
400-AL | 0.0778 | 0.705 | cs | 400 | 0.00403
1200-AL | 0.0247 | 1.371 | cs | 1200 | 0.00403
2400-AL | 0.0121 | 2.066 | cs | 2400 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_changer_type | trafo_characteristic_table
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | Ratio | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | Ratio | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_changer_type | trafo_characteristic_table
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2 | Ratio | FALSE
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2 | Ratio | FALSE

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | bus | geo | object
6 | load | name | object
7 | load | bus | uint32
8 | load | p_mw | float64
9 | load | q_mvar | float64
10 | load | const_z_p_percent | float64
11 | load | const_i_p_percent | float64
12 | load | const_z_q_percent | float64
13 | load | const_i_q_percent | float64
14 | load | sn_mva | float64
15 | load | scaling | float64
16 | load | in_service | bool
17 | load | type | object
18 | gen | name | object
19 | gen | bus | uint32
20 | gen | p_mw | float64
21 | gen | vm_pu | float64
22 | gen | sn_mva | float64
23 | gen | min_q_mvar | float64
24 | gen | max_q_mvar | float64
25 | gen | scaling | float64
26 | gen | slack | bool
27 | gen | controllable | bool
28 | gen | id_q_capability_characteristic | Int64
29 | gen | reactive_capability_curve | bool
30 | gen | curve_style | object
31 | gen | in_service | bool
32 | gen | slack_weight | float64
33 | gen | type | object
34 | gen | min_p_mw | float64
35 | gen | max_p_mw | float64
36 | gen | source_type | object
37 | ext_grid | name | object
38 | ext_grid | bus | uint32
39 | ext_grid | vm_pu | float64
40 | ext_grid | va_degree | float64
41 | ext_grid | slack_weight | float64
42 | ext_grid | in_service | bool
43 | ext_grid | controllable | bool
44 | line | name | object
45 | line | std_type | object
46 | line | from_bus | uint32
47 | line | to_bus | uint32
48 | line | length_km | float64
49 | line | r_ohm_per_km | float64
50 | line | x_ohm_per_km | float64
51 | line | c_nf_per_km | float64
52 | line | g_us_per_km | float64
53 | line | max_i_ka | float64
54 | line | df | float64
55 | line | parallel | uint32
56 | line | type | object
57 | line | in_service | bool
58 | line | geo | object
59 | line | thermal_role | object
60 | trafo | name | object
61 | trafo | std_type | object
62 | trafo | hv_bus | uint32
63 | trafo | lv_bus | uint32
64 | trafo | sn_mva | float64
65 | trafo | vn_hv_kv | float64
66 | trafo | vn_lv_kv | float64
67 | trafo | vk_percent | float64
68 | trafo | vkr_percent | float64
69 | trafo | pfe_kw | float64
70 | trafo | i0_percent | float64
71 | trafo | shift_degree | float64
72 | trafo | tap_side | object
73 | trafo | tap_neutral | float64
74 | trafo | tap_min | float64
75 | trafo | tap_max | float64
76 | trafo | tap_step_percent | float64
77 | trafo | tap_step_degree | float64
78 | trafo | tap_pos | float64
79 | trafo | tap_changer_type | object
80 | trafo | id_characteristic_table | Int64
81 | trafo | tap_dependency_table | bool
82 | trafo | parallel | uint32
83 | trafo | df | float64
84 | trafo | in_service | bool
85 | trafo | oltc | bool

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 3.4.0 | 3.1.0 | FALSE | FALSE | KE_JICA_2012_Base | 50 | 100